## Battery Calculations
Battery Capacity Calculator Instructions: 1) Select the AES model from the AES Model field. 2) Select if Intellipro is installed 3) Select if Ethernet Cable is installed during normal operation. (Only applies to 2.0 subscribers) 4) Select if 7762 is installed (Only applies to 7788F) 5) Enter the # of hours of backup time required. AES products are UL listed for 24 hours operation on battery backup. 6) The calculator will return the recommended minumum battery capacity and max primary input DC and AC current
BACKUP BATTERY CALCULATIONS | [8 empty] | PRIMARY POWER CALCULATIONS
AES Model |  | 7794 Ipro Installed |  |  |  | 7762 Installed |  | # Hours Backup Time | Standby Current (Amps) |  | Intellipro Current (Amps) |  | Ethernet Current (Amps) |  | 7762 Current (Amps) |  | Standby 24VDC Current (Amps)
7788F |  | No |  | No |  | Yes |  | 24 | 0.186 | + | 0 | + | 0 | + | 0.015 | = | 0.201
Standby Current (Amps) |  | Intellipro Current (Amps) |  | Ethernet Current (Amps) |  | 7762 Current (Amps) |  | Total Standby Current (Amps) | Transmit Current (Amps) |  | Intellipro Current (Amps) |  | Ethernet Current (Amps) |  | 7762 Current (Amps) |  | Max 24VDC Current (Amps)
0.149 | + | 0 | + | 0 | + | 0 | = | 0.149 | 0.914 | + | 0 | + | 0 | + | 0.015 | = | 0.929
# Hours Backup Time |  | Standby Current (Amps) |  | Required Standby Capacity (Amp-Hours) |  |  |  |  | Standby Current (Amps) |  | Intellipro Current (Amps) |  | Ethernet Current (Amps) |  | 7762 Current (Amps) |  | Standby 16VAC Current (Amps)
24 | x | 0.149 | = | 3.576 |  |  |  |  | 0.32 | + | 0 | + | 0 | + | 0.015 | = | 0.335
Transmit/Alarm Current (Amps) |  | Required Alarm Time (Hours) |  | Required Alarm Capacity (Amp-Hours) |  |  |  |  | Transmit Current (Amps) |  | Intellipro Current (Amps) |  | Ethernet Current (Amps) |  | 7762 Current (Amps) |  | Max 16VAC Current (Amps)
0.728 | x | 0.25 | = | 0.182 |  |  |  |  | 1.367 | + | 0 | + | 0 | + | 0.015 | = | 1.382
Required Standby Capacity (Amp-Hours) |  | Required Alarm Capacity (Amp-Hours) |  | Total Required Backup Capacity (Amp-Hours)
3.576 | + | 0.182 | = | 3.758
Total Required Backup Capacity (Amp-Hours) |  | Recommended Safety Factor |  | Recommended Minimum Battery Capacity (Amp-Hours) *** |  | *** The battery requirements presented here are only AES recommendations. For UL listed battery requirements please read the product Installation and Operation Manual.
3.758 | x | 120% | = | 4.5096
Updated 7/27/2022
Note on C14: MODEL: Please select your AES Subscriber model.
Note on E14: Intellipro: Select whether Intellipro is installed during normal operation.
Note on G14: Ethernet: Select whether Ethernet cable is connected during normal operation.
Note on I14: 7762 Select whether 7762 board is connected during normal operation.
Note on K14: Standby Hours: Enter the number of total hours required for Standby time. AES products are UL listed for 24 hours.

## Sheet1
|  | BATTERY | [5 empty] | 24VDC | [5 empty] | 16VAC
Subscriber Type | IPRO Type | standby | transmit | ipro | enet | 7762 |  | standby | transmit | ipro | enet | 7762 |  | standby | transmit | ipro | enet | 7762
None |  | 0 | 0 | 0 | 0 | 0
7007 | 7094A Ipro Installed | 0.166 | 0.79 | 0.145 | 0.015 | 0 |  | 0.21 | 0.886 | 0.145 | 0.015 | 0 |  | 0.316 | 1.459 | 0.22 | 0.022 | 0
7707 | 7794A Ipro Installed | 0.175 | 0.752 | 0.165 | 0.015 | 0 |  | 0.21 | 0.899 | 0.16 | 0.015 | 0 |  | 0.35 | 1.42 | 0.265 | 0.024 | 0
7177 | 7794A Ipro Installed | 0.176 | 0.886 | 0.16 | 0.015 | 0 |  | 0.205 | 1.017 | 0.16 | 0.015 | 0 |  | 0.36 | 1.6 | 0.243 | 0.022 | 0
7058E | 7094 Ipro Installed | 0.136 | 0.75 | 0.145 | 0 | 0 |  | 0.153 | 0.822 | 0.148 | 0 | 0 |  | 0.295 | 1.178 | 0.22 | 0 | 0
7788F | 7794 Ipro Installed | 0.149 | 0.728 | 0.16 | 0 | 0.015 |  | 0.186 | 0.914 | 0.167 | 0 | 0.015 |  | 0.32 | 1.367 | 0.244 | 0 | 0.015
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19